## Spot size ratio - m
Single-pixel measurement or ‘theoretical spot size ratio’
Instructions
ONLY CHANGE GREEN FIELDS !
Calculator
INPUT |  |  | RESULTS
Detector resolution |  |  | IFOV
Hor | 384 |  |  | # Pixels square
Vert | 288 |  |  | 5 |  | Set # pixels: 3 pixels minimum, CNPP 5 pixels minimum
FOV |  |  | mrad
HFOV (°) | 22 |  | 0.99993 | 4.9996
VFOV (°) | 16 |  | mm
Distance |  |  | 11.9991 | 5.9996 |  | Minimum spot size in cm that that camera can measure at set 'Distance '
in m | 12 |  | Theoretical max. distance (m)
|  |  | 100.0072 |  |  | Theorethical max. distance (m) of a 50 x 50 cm square. Max distance for CNPP approved use
|  |  | D max | "n" cm
|  |  | 100.0072 | 50 |  | Theorethical max. distance (m) of a n x n cm square.
Horizontal FOV (m) |  |  | 4.6651 |  |  | Horizontal FOV (m) based on horizontal ° FOV of the selected lens
Vertical FOV (m) |  |  | 3.373 |  |  | Vertical FOV (m) based on vertical ° FOV of the selected lens
SUMMARY |  |  |  | m/ft: | 3.2808
| Hor. FOV | Max. distance (m) |  | Max. distance (ft)
|  | 5x5 pixels | 3x3 pixels | 5x5 pixels | 3x3 pixels
FTD-2216-S | 22° | 100 | 167 | 328.084 | 547.9003
FTD-4231-S | 42° | 52 | 87 | 170.6037 | 285.4331
FTD-8865-S | 88° | 25 | 42 | 82.021 | 137.7953
| @5x5 max D. | HOR FOV Meter | VERT FOV Meter | HOR FOV Feet | VERT FOV Feet
FTD-2216-S | 22° | 38.9 | 28.1 | 127.6247 | 92.1916
FTD-4231-S | 42° | 39.9 | 28.8 | 130.9055 | 94.4882
FTD-8865-S | 88° | 48.3 | 31.9 | 158.4646 | 104.6588